Cape Fear Public Utility Authority

Application for Authorization to Construct

Grease Interceptor for a Food Service Establishment

Prior to construction of a grease interceptor that will be connected to the CFPUA sewer system an Authorization to Construct (AtC) must be issued by Community Compliance. Grease Interceptors must comply with NC Plumbing Code and CFPUA grease interceptor technical specifications.

| Name of Business: |  |
| --- | --- |
| Corporation or Proprietor: |  |
| Sewer Service Address: |  |
| Mailing Address: |  |
| City, State, & Zip |  |
| Phone: |  |
| Fax: |  |
| Email address: |  |
| Description (planed hours, type of food service, and type of menu): |  |
| Consultant’s Name & Co.: |  |
| Mailing Address: |  |
| City, State, & Zip |  |
| Phone: |  |
| Fax: |  |
| Email address: |  |

Attach:

- Plan showing the size and location of the grease interceptor.

- A manufacturer, model, and manufacturer’s specifications for the grease interceptor.

- Plan showing all fixtures draining to the grease interceptor.

- Table of the fixtures, fixture trap sizes, and drainage fixture units.

Plans may be preliminary; however the application must be amended if plan revisions change the location or size of the interceptor, fixtures, trap sizes, or drainage fixture units

I certify that this application and the attachments are true, complete, and accurate to the best of my knowledge and belief.

Signature of Consultant      Type of Consultant, License # (i.e. Architect, Engineer, Plumber)	Date

Signature of Authorized Representative 		Title					Date

An Authorized Representative is a sole proprietor, corporate partner, or a person responsible for principle business decisions.

Submit to:

CFPUA, Community Compliance

235 Government Center Dr.

Wilmington, NC 28405

Phone:	(910) 332-6558

Email:	Community.Compliance@cfpua.org

Cape Fear Public Utility Authority

Technical Standards

GREASE INTERCEPTOR DESIGN CRITERIA

- Shall be approved by the Community Compliance Supervisor or designee. The application for authorization to construct  shall be signed by the owner, proprietor or responsible official, and include:

  - Contact information for the owner, proprietor or responsible official

  - Address of the facility

  - A drawing showing the location of the building, kitchen, interceptor, and traffic ways.

  - The manufacturer’s model number and specifications.

  - A list of all plumbing fixtures plumbed to the interceptor including the drainage fixtures units (DFU) and trap size of each fixture.

- Shall be in-ground, exterior installation, and readily accessible for unhindered maintenance and inspection

- Shall be sized to achieve a minimum 20 minute detention-time.  Interceptor volume required to achieve 20 minute detention-time is calculated by: V=Q X 20

  - V is the required wetted volume of interceptor in gallons

  - Q is theoretical flow rate into the interceptor in gallons per minute (GPM).  The theoretical flow rate is determined by summing the DFUs, as specified in the International Plumbing Code (IPC), of all fixtures plumbed to the interceptor and converting to GPM (2 DFU = 1 GPM). For automatic dishwashers and similar fixtures the manufacturer’s discharge flow rating may be used.

- Shall have inlet and outlet tees.  The inlet tee shall be sized to match the service (a minimum of 3 inches in diameter) and the length shall extend 25% (20% to 30% allowed) into the liquid depth. The outlet tee shall be 6 inches in diameter and the length shall extend 50% (45% to 55% allowed) into the liquid depth.

- Shall have a means to slow the flow to avoid short-circuiting, such as a baffle system and dual sweep tee.

- Shall have at least 9 inches of freeboard above the liquid surface.

- Shall have access openings over the inlet, outlet, and each compartment within the grease interceptor.  Each opening shall be twenty-four (24) inches in diameter and contain pick holes.  Shall be stormwater infiltration proof. Manholes or covers shall extend to the finished grade.

- Shall be designed to handle traffic-bearing loads when located in vehicular travel ways. Interceptors in non-vehicular areas shall be at least pedestrian load bearing.

- Shall be vented in accordance with the IPC as adopted by North Carolina.

- Plumbing fixtures connected to the interceptor shall have baskets, screens, or other intercepting devices to prevent passage into the drainage system of solids ½ inch or larger in size.  The baskets, screens, or devices shall be removable for cleaning purposes.

- Waste from food grinders shall discharge through a solids interceptor prior to entering the grease interceptor.  All other fixtures and drains (except those not exposed to grease laden sources) receiving kitchen or food preparation wastewater shall pass through the grease interceptor.

- Interceptors that are cast-in-place, masonry tanks, or not a manufactured grease interceptor shall be designed by a professional engineer licensed by North Carolina.

- A proposed nonconventional interceptor may be evaluated and approved on a case by case basis contingent upon proper sizing and documentation demonstrating grease removal efficiencies are equivalent to a conventional interceptor.

A request to install an interior interceptor, interior trap or automatic grease removal devices shall include a design plan certified by a professional architect, engineer or plumber, licensed by North Carolina, demonstrating that there is inadequate space for exterior installation. Inadequate space considerations include: legal property boundary restrictions, utility conflicts that cannot be relocated, proximity to the building and its foundation, or overhead obstacles.

Instructions

- Complete the application.

- Create a simple table showing the number and sizes of all drains that will be going to the grease interceptor.

- Submit the application and table to the address listed on the application.

- An Environmental Compliance Officer will calculate the minimum size grease interceptor needed and will email you the size. At that point, you may begin looking for manufacturers with grease interceptors meeting the design criteria listed on page two.

- Once an interceptor is chosen, send the Environmental Compliance Officer the manufacturer, model and size. Also send a simple drawing showing the location of the interceptor in relationship to the establishment along with a plan showing all fixtures draining to the interceptor.

- If all requirements are met, the Environmental Compliance Officer will issue the Authorization To Construct (AtC). Keep the AtC on site and available during the construction for review by inspectors.